CHAPTER 3.  INITIAL COSTS, SERVICE LIFE AND ANNUAL EXPENSE

FACTORS OF FACILITIES AND EQUIPMENT

3-1.   GENERAL.  Tabulations are included for estimated service life

and annual expense factors of equipment and facilities for

lighting, refrigeration, cooking, domestic hot water and space

heating to be used to compare relevant alternative utility

combinations only.  The tabulations are approximate national

averages and should be used as a guide in preparing the life-

cycle cost of utility systems described in Chapter l.  The

tabulations may be used in preparing Form HUD-5l994 if they

correspond to local conditions.  The tabulations should be

adjusted if local conditions differ.  The tabulations should

not be used for budgeting purposes, establishing rental

schedules or estimating construction costs.

3-2.   INITIAL COSTS AND SERVICE LIFE.

a.   Initial costs should be obtained from the equipment

manufacturer, architect/engineer, or the HUD Field

Office.  In the absence of actual local cost data, use

commercially available cost estimation guides.

b.   The service life in years are for properly designed,

installed and maintained equipment for the particular

conditions.  These years should not be modified unless

local experience has the approximate average service life

of the facility.  For example, equipment in projects

built during the past ten years should have incurred a

portion of their normal service life and would not

necessarily indicate the average annual replacement

expense over a 20-year period, the study-life of the

analysis.

3-3.   ANNUAL CHARGES FOR REPLACEMENT.  The annual expense factors

for replacement are a percent of the initial cost.  If initial

cost percentages were deposited each year in a Sinking Fund at

5 percent interest, enough money would accumulate to replace

the equipment at the end of the service life.  If local

experience indicates service life different from those listed,

the following tabulations may be used:

Page 3-1

12/85

_____________________________________________________________________

Annual                 Annual                    Annual

Service       Expense     Service    Expense      Service    Expense

Life-Yrs.     Factor      Life-Yrs.  Factor       Life-Yrs.    Factor

1         100.00         15       4.63           29         1.60

2          48.76         16       4.23           30         1.51

3          31.72         17       3.87           31         1.41

4          23.20         18       3.55           32         1.33

5          18.10         19       3.27           33         1.25

6          14.70         20       3.02           34         1.18

7          12.28         21       2.80           35         1.11

8          10.47         22       2.60           36         1.04

9           9.07         23       2.41           37         0.98

10          7.95         24       2.25           38         0.93

11          7.04         25       2.10           39         0.88

12          6.28         26       1.96           40         0.83

13          5.65         27       1.83           50         0.48

14          5.10         28       1.71

3-4.   PROCEDURE FOR MAKING ADJUSTMENTS.  A facility or an equipment

item may be modified based on local conditions as stated in

paragraph 3-3, but a corresponding adjustment must be made in

the annual charges for replacement.

a.   If a change is made in initial cost but not in service

life, the new initial cost is multiplied by the annual

expense factor to obtain the adjusted annual charges for

replacement for dollars per dwelling unit.

b.   If a service life change is made, the corresponding

annual expense factor for replacements is selected from

paragraph 3-3.  The initial equipment cost is multiplied

by the new annual expense factor to obtain the new annual

charges for dollars per dwelling unit.

c.   The annual expense factors should not be modified because

of local experience unless the approximate average

service life of the considered facility is covered.

3-5.   ANNUAL EXPENSES FOR MAINTENANCE AND REPAIRS.  The annual-

expense factors for maintenance and repairs are a percent of

the initial costs and are averaged over the equipment's

service life.  If local experience indicates that the annual

expenses for maintenance and repair are significantly

different from the amount determined by multiplying the

annual-expense factor times the initial costs, then locally

developed factors should be utilized.

12/85                            Page 3-2

_____________________________________________________________________

TABLE I

ELECRICAL SYSTEM

Annual-Expense Factors

Estimated                 Maint.

Equipment and       Service Life   Replace-   and

Service Life         in Years      ments      Repairs        Total

Substation

Outdoor              40          0.83%      1.50%          2.33%

Indoor               40          0.83       1.16           1.99

Exterior Distribution

Overhead             24          2.25       1.25           3.50

Underground          26          1.96       1.24           3.20

Interior Wiring        37          0.98       1.82           2.80

Checkmeters            20          3.02       4.00           7.02

TABLE II

NATURAL GAS SYSTEMS

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment  in Years      Ments      Repairs      Total

Exterior Distribution     20         3.02%      1.00% 2/     4.02% 1/

Interior Piping           40         0.83       0.50         1.33

Checkmeters               30         1.51       3.50  2/     5.01 2/

1/   This table covers only the additional facilities

necessary to supply domestic hot water from a project-

operated space heating system.  Where a complete and

separate project-operated domestic hot water system is

proposed, the initial costs of the necessary boilers and

other heating equipment will be approximately 30 percent

of the values shown for such items in Table IV.

2/   Installation of this equipment may justify the use of

demand limiting devices.  The cost of such devices should

be added to these costs.

Page 3-3                            12/85

_____________________________________________________________________

TABLE III

PROJECT OPERATED DOMESTIC HOT WATER EQUIPMENT

Annual Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment      in years     ments      Repairs      Total

Boilers and Auxiliaries 1/

Storage Tanks With

heater coils              20          3.02%      2.00%        5.02%

Circulating Pumps           15          4.63       2.00         6.63

Exterior Piping System

(copper tubing)

Fabricated Conduit        20          3.02       2.00         5.02

Concrete Trench           30          1.51       1.25         2.76

Interior Piping

in Buildings

Galvanized Steel          20          3.02       2.50         5.52

Galvanized W.I.           20          3.02       2.50         5.52

Copper                    40          0.83       2.00         2.83

Electric Storage Water

Heaters with Lined Tanks 2/

Row Houses and

Apartments                20          3.02       1.00         4.02

Hi-Rise Apartments        20          3.02       1.00         4.02

1/   This table covers only the additional facilities

necessary to supply domestic hot water from a project-

operated space heating system. Where a complete and

separate project-operated domestic hot water system is

proposed, the initial costs of the necessary boilers and

other heating equipment will be approximately 30% of the

values shown for such items in Table IV.

2/   Installation of this equipment may justify the use of

demand limiting devices.  The cost of such devices should

be added to these costs.

12/85                         Page 3-4

_____________________________________________________________________

TABLE IV

PROJECT OPERATED SPACE HEATING EQUIPMENT

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment     in years      ments      Repairs      Total

Boilers and Auxiliaries

Except Fuel Firing

Equipment 1/

Low Pressure Steam or

Forced Hot Water            30        1.51%      1.50%        3.01%

High Pressure Steam         30        1.51       1.50         3.01

Fuel Firing Equipment 1/

Gas Burner                  25        2.10       1.00         3.10

Oil Burner (Light Oil)      25        2.10       1.50         3.60

Oil Burner (Heavy Oil) 2/   25        2.10       2.00         4.10

Exterior Piping System

(Fabricated Conduit Methods

or Concrete Trenches)

If possible, lay out system

and make preliminary estimate

of cost.  Otherwise the following

figures, when properly adjusted

may be used for estimating:

Two-Story Buildings         20        3.02       2.00         5.02

Three-Story Buildings       20        3.02       2.00         5.02

Multi-Story Buildings       20        3.02       2.00         5.02

Piping, Radiators and

Specialties in buildings      40        0.83       1.25         2.08

Electrical Work               37        0.98       1.82         2.80

1/     Includes capacity for domestic hot water.  For space heating

only, use 70% of the applicable amounts.  Cost for oil

equipment includes cost for oil storage tanks.

2/     Add 20% for Combination Gas-Oil burner.

Page 3-5                             12/85

_____________________________________________________________________

TABLE V

INDIVIDUAL DWELLING DOMESTIC HOT WATER EQUIPMENT

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-    and

Facility or Equipment      in years     ments      Repairs      Total

Automatic Storage Water

Heaters(30 Gallons) 1/

Gas

Lined Tank 2/               10        7.95%       1.00%       8.95%

Oil

Lined Tank 2/               12        6.28        2.25         8.53

Electric

Lined Tank 2/               10        7.95        1.00         8.95

Storage Tank (30 Gallons)

Lined Tank 2/               20        3.02        1.00         4.02

Indirect Coil in Boiler     20        3.02        1.00         4.02

Hot Water Piping

Galvanized Steel          20        3.02        2.50         5.52

Galvanized W.I.           20        3.02        2.50         5.52

Copper                    40        0.83        2.00         2.83

1/     Heaters of the same storage capacity but with different fuels

may not produce the same amount of hot water per hour.  The

size of the heater should be checked for adequacy of hot water

supply and conformance to utility company requirements, and

costs adjusted as necessary.

2/     Cement, glass, porcelain, or similar lining.

12/85                          Page 3-6

_____________________________________________________________________

TABLE VI

INDIVIDUAL DWELLING SPACE HEATING EQUIPMENT

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment     in years      ments      Repairs      Total

Space (Room) Heater

Electric                    15         4.63%       1.00%      5.63%

Gas                         15         4.63        2.00       6.63

Oil                         12         6.28        2.50       8.78

Wall Furnace (Recessed

heaters)

Gas                         15         4.63        2.03       6.66

Forced Warm Air System

Gas

Furnace with integral

burner, blower

and controls               20         3.02       1.50        4.52

Duct Work                  30         1.51       1.00        2.51

Elect. Conn.               30         1.51       0.50        2.01

Oil

Furnace with integral

burner, blower

and controls              20          3.02       1.75        4.77

Duct Work                 30          1.51       1.00        2.51

Elect. Conn.              30          1.51       0.50        2.01

Oil Tank and Piping       20          3.02       1.50        4.52

Hot Water System

Gas

Complete System with

integral boiler-burner

unit and controls         30          1.51%      1.25%       2.76

Pump                       15          4.63       2.00        6.63

Elect. Conn.               30          1.51       0.50        2.01

Page 3-7

12/85

_____________________________________________________________________

TABLE VI (Con't)

INDIVIDUAL DWELLING SPACE HEATING EQUIPMENT

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment      in Years     ments      Repairs      Total

Oil

Complete System without

burner, with controls       30        1.51       1.25        2.76

Burner                       20        3.02       2.00        5.02

Pump                         15        4.63       2.00        6.63

Elect. Conn.                 30        1.51       0.50        2.01

Oil Tank and Piping          20        3.02       1.50        4.52

Electric (Exc. Wiring)

Baseboard                     40        0.82       0.50        1.32

Ceiling Cable                 40        0.82       0.50        1.32

Forced Air Wall Heaters       20        3.02       1.00        4.02

Package Furnace

(Exc. Ducts)

w/dx Elec. Cooling            20        3.02       1.50        4.52

Heat Pump (inc.

Cooling)                     11        7.04      10.00       17.04

Hydronic Boiler               20        3.02       1.25        4.27

Package Terminal

(Heating and Cooling)        15        4.63      10.00       14.63

12/85                         Page 3-8

_____________________________________________________________________

TABLE VII

STRUCTURAL AND RELATED ITEMS

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment      in Years      ments     Repairs      Total

Additional Roads for

Fuel Deliveries                40         0.83%     .50%        1.33%

Boiler Rooms

in Basement of Dwelling

Buildings (Including stack)

(Up to 200 DU) 1/

Oil or Gas Fired             40         0.83      .50         1.33

Furnace Room in Dwelling       40         0.83      .50         1.33

Full Basements 2/

Under 3-StoryBldg.           40         0.83      .50         1.33

Crawl Spaces (3' - 0")

Under2-StoryBldg.            40         0.83      .50         1.33

prefabricated Flues - Metal

All Fuels (One-and Two-Story) 20         3.02      .50         3.52

Prefabricated Flues - Ceramic

All Fuels (One-and Two-Story) 30         1.51      .50         2.01

1/  For larger boiler rooms or for central plants, sketches

should be prepared for estimated costs.

2/  Additional cost over that of a floor slab on the ground.

Page 3-9

12/85

_____________________________________________________________________

TABLE VII  (Cont')

STRUCTURAL AND RELATED ITEMS

Annual-Expense Factors

Estimated                Maint.

Service Life  Replace-   and

Facility or Equipment      in Years      ments     Repairs      Total

Flues (Continued)

Single 8" x 8" Masonry

1-Story Flat Roof         40           0.83%       .79%      1.62%

1-Story Pitch Roof        40           0.83        .63       1.46

2-Story Flat Roof         40           0.83        .53       1.36

2-Story Pitch Roof        40           0.83        .48       1.31

Add for Basement          40           0.83        .50       1.33

Two 8" x 8" Masonry

(for two dwellings)

1-Story Flat Roof         40           0.83        .75       1.58

1-Story Pitch Roof        40           0.83        .59       1.42

2-Story Flat Roof         40           0.83        .50       1.33

2-Story Pitch Roof        40           0.83        .42       1.25

Add for Basement          40           0.83        .50       1.33

One 8" x 8" and one

8"x 4" Masonry (for

two dwellings)

1-Story Flat Roof         40           0.83        .89       1.72

1-Story Pitch Roof        40           0.83        .74       1.57

2-Story Flat Roof         40           0.83        .58       1.41

2-Story Pitch Roof        40           0.83        .47       1.30

Add for Basement          40           0.83        .50       1.33

Two 8" x 8" and two

8"x 4" Masonry (for

two dwellings)

1-Story Flat Roof         40           0.83        .70       1.53

1-Story Pitch Roof        40           0.83        .53       1.36

2-Story Flat Roof         40           0.83        .45       1.28

2-Story Pitch Roof        40           0.83        .38       1.21

Add for Basement          40           0.83        .50       1.33

12/85                          Page 3-10

_____________________________________________________________________

Table VIII

COOKING AND AIR-CONDITIONING EQUIPMENT

Annual-Expense Factors

Estimated                Maint.

Facility or               Service Life  Replace-   and

Equipment                  in years      ments     Repairs      Total

Ranges

Electric                     10          7.95       3.13       11.08

Gas                          10          7.95       2.50       10.45

Electric Air

Conditioning Systems

Thru-Wall-l5,OOO

BTU (a),(b),(c)            10          7.95       5.0        12.95

Central Dwelling

Unit - 1 1/2 - 2 Ton

(a)(b)                     15          7.95       10.0       17.95

Heat Pump (a),(b),(c)      15          7.04       10.0       17.04

Package Terminal

Heating & Cooling          15          4.63       10.0       14.63

Electric Motor

Compressor With

Chiller (b),(c)            20          3.02        5.0        8.02

Gas Air Conditioning

Systems - Air Cooled

Absorption

Heating & Cooling          15          4.63       10.0       14.63

Water Cooled Absorption

25 to 100 Tons

(b),(c)1/                  20          3.02        5.0        8.02

(a) Single & Twin Houses

(b) Row Houses and Garden Apartments

(c) Hi-Rise Apartments

1/  Chiller and piping added to high temperature or steam

boiler.

Page 3-11                        5/95

_____________________________________________________________________